Features transformers 500/220 kV and 220/110 kV substations

| Area | Nominal output of the primary winding | Nominal output of the secondary winding | Nominal output of the third winding | Nominal voltage of the primary winding | Nominal voltage of the secondary winding | Nominal voltage of the third winding | Resistance to short circuit [Z12] | Resistance to short circuit [Z23] | Resistance to short circuit [Z31] | Copper loss [pCu12] | Copper loss [pCu23] | Copper loss [pCu31] | Magnetizing current | Core loss | (точка обмотки переключателя ответвлений) | The amplitude of the position of the tap changer | Макс. кол-во ответвлений направляющихся вниз | Макс. кол-во ответвлений направляющихся вверх | winding 1 | Winding 2 | Winding 3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | [MVА] | [MVА] | [MVА] | [kV] | [kV] | [kV] | [%] | [%] | [%] | [кW] | [кW] | [кW] | [%] | [кW] |  | [%] |  |  | winding 1 | Winding 2 | Winding 3 |
| Regar | 3х267 | 267 | 67 | 500/√3 | 220/√3 | 38.5 | 8.3 | 23.1 | 12.4 | 438 | 76.5 | 63 | 0.11 | 175 | 1 | 1.4 | 8 | 8 | Y0 | Auto | D-0-11 |
|  | 3х267 | 267 | 67 | 500/√3 | 220/√3 | 38.5 | 8.3 | 23.1 | 12.4 | 438 | 76.5 | 63 | 0.11 | 175 | 1 | 1.4 | 8 | 8 | Y0 | Auto | D-0-11 |
|  | 3х267 | 267 | 67 | 500/√3 | 220/√3 | 38.5 | 11.3 | 36.3 | 23 | 470 | 86.6 | 78.3 | 0.11 | 292.7 | 1 | 1.4 | 8 | 8 | Y0 | Auto | D-0-11 |
| Dushanbe | 3х167 | 167 | 63 | 500/√3 | 230/√3 | 36 | 12.5 | 43.7 | 28.8 | 285.7 | 97.4 | 99.9 | 0.09 | 61.6 | 1 | 1.25 | 8 | 8 | Y0 | Auto | D-0-11 |
| Sugd | 3х167 | 167 | 63 | 500/√3 | 230/√3 | 36 | 12.5 | 43.7 | 28.8 | 285.7 | 97.4 | 99.9 | 0.09 | 61.6 | 1 | 1.25 | 8 | 8 | Y0 | Auto | D-0-11 |
|  | 3х167 | 167 | 63 | 500/√3 | 230/√3 | 36 | 12.5 | 43.7 | 28.8 | 285.7 | 97.4 | 99.9 | 0.09 | 61.6 | 1 | 1.25 | 8 | 8 | Y0 | Auto | D-0-11 |
| Ravshan | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 275 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 20 | 20 | 20 | 230 | 38.5 | 11 | 12.6 | 18.9 | 63 | 135.3 | 148.8 | 106.4 | 2.92 | 79 | 3 | 1.2 | 10 | 10 | Y0 | Auto | D-0-11 |
| Novaya | 200 | 200 | 80 | 230 | 121 | 11 | 11 | 32 | 20 | 430 | 360 | 320 | 0.5 | 125 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 200 | 200 | 80 | 230 | 121 | 11 | 11 | 32 | 20 | 430 | 360 | 320 | 0.5 | 125 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Shahrinav | 125 | 125 | 62.5 | 230 | 121 | 10.5 | 13.5 | 24.19 | 8.4 | 386 | 133.38 | 94.19 | 0.12 | 88 | 1 | 1.25 | 8 | 8 | Y0 | Y | D-0-11 |
|  | 125 | 125 | 62.5 | 230 | 121 | 10.5 | 13.5 | 24.19 | 8.4 | 386 | 133.38 | 94.19 | 0.12 | 88 | 1 | 1.25 | 8 | 8 | Y0 | Y | D-0-11 |
| Jangal | 200 | 200 | 80 | 230 | 121 | 11 | 11 | 32 | 20 | 430 | 360 | 320 | 0.5 | 125 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 200 | 200 | 80 | 230 | 121 | 11 | 11 | 32 | 20 | 430 | 360 | 320 | 0.5 | 125 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Orjabad-2 | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Rogun | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Rumi | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.8 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Geran | 63 | 63 | 32 | 230 | 121 | 11 | 11.1 | 34.9 | 21.31 | 157.1 | 192.4 | 160.3 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y0 | Auto | D-0-11 |
|  | 63 | 63 | 32 | 230 | 121 | 11 | 11.1 | 34.8 | 21.31 | 157.1 | 192.4 | 160.3 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y0 | Auto | D-0-11 |
| Pryadilnaya | 63 | 63 | 32 | 230 | 121 | 11 | 11.1 | 34.8 | 21.31 | 157.1 | 192.4 | 160.3 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.8 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Kolhozobod | 63 | 63 | 32 | 230 | 121 | 11 | 11.1 | 34.8 | 21.31 | 157 | 192.4 | 160.3 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y0 | Auto | D-0-11 |
|  | 63 | 63 | 32 | 230 | 121 | 11 | 11.1 | 34.8 | 21.31 | 157.1 | 192.4 | 160.3 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y0 | Auto | D-0-11 |
| Lolazor | 125 | 125 | 62.5 | 230 | 121 | 10.5 | 13.5 | 24.19 | 8.4 | 386 | 133.38 | 94.19 | 0.12 | 88 | 1 | 1.25 | 8 | 8 | Y0 | Y | D-0-11 |
|  | 125 | 125 | 62.5 | 230 | 121 | 10.5 | 13.5 | 24.19 | 8.4 | 386 | 133.38 | 94.19 | 0.12 | 88 | 1 | 1.25 | 8 | 8 | Y0 | Y | D-0-11 |
| Dangara | 125 | 125 | 62.5 | 230 | 121 | 10.5 | 13.5 | 24.19 | 8.4 | 386 | 133.38 | 94.19 | 0.12 | 88 | 1 | 1.25 | 8 | 8 | Y0 | Y | D-0-11 |
|  | 125 | 125 | 62.5 | 230 | 121 | 10.5 | 13.5 | 24.19 | 8.4 | 386 | 133.38 | 94.19 | 0.12 | 88 | 1 | 1.25 | 8 | 8 | Y0 | Y | D-0-11 |
| Hatlon | 125 | 125 | 62.5 | 230 | 121 | 10.5 | 13.5 | 24.19 | 8.4 | 386 | 133.38 | 94.19 | 0.12 | 88 | 1 | 1.25 | 8 | 8 | Y0 | Y | D-0-11 |
|  | 125 | 125 | 62.5 | 230 | 121 | 10.5 | 13.5 | 24.19 | 8.4 | 386 | 133.38 | 94.19 | 0.12 | 88 | 1 | 1.25 | 8 | 8 | Y0 | Y | D-0-11 |

Features transformers 500/220 kV and 220/110 kV substations

| Area | Nominal output of the primary winding | Nominal output of the secondary winding | Nominal output of the third winding | Nominal voltage of the primary winding | Nominal voltage of the secondary winding | Nominal voltage of the third winding | Resistance to short circuit [Z12] | Resistance to short circuit [Z23] | Resistance to short circuit [Z31] | Copper loss [pCu12] | Copper loss [pCu23] | Copper loss [pCu31] | Magnetizing current | Core loss | (точка обмотки переключателя ответвлений) | The amplitude of the position of the tap changer | Макс. кол-во ответвлений направляющихся вниз | Макс. кол-во ответвлений направляющихся вверх | winding 1 | Winding 2 | Winding 3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | [MVА] | [MVА] | [MVА] | [kV] | [kV] | [kV] | [%] | [%] | [%] | [кW] | [кW] | [кW] | [%] | [кW] |  | [%] |  |  | winding 1 | Winding 2 | Winding 3 |
| Yavan | 40 | 40 | 40 | 230 | 38.5 | 6.6 | 12.4 | 22.73 | 9.54 | 201.5 | 237.1 | 177 | 0.54 | 62.1 | 3 | 1 | 12 | 12 | Y0 | Y0 | D-0-11 |
|  | 40 | 40 | 40 | 230 | 38.5 | 6.6 | 12.4 | 22.73 | 9.54 | 201.5 | 237.1 | 177 | 0.54 | 62.1 | 3 | 1 | 12 | 12 | Y0 | Y0 | D-0-11 |
| Shar-shar | 25 | 25 | 25 | 230 | 38.5 | 11 | 12.7 | 10.1 | 6.3 | 130 | 135 | 105 | 1 | 53 | 3 | 1 | 12 | 12 | Y0 | Y0 | D-0-11 |
|  | 25 | 25 | 25 | 230 | 38.5 | 11 | 12.7 | 10.1 | 6.3 | 130 | 135 | 105 | 1 | 53 | 3 | 1 | 12 | 12 | Y0 | Y0 | D-0-11 |
| Sebiston | 25 | 25 | 25 | 230 | 38.5 | 6.6 | 12.7 | 10.1 | 6.3 | 130 | 135 | 105 | 0.9 | 50 | 1 | 1 | 12 | 12 | Y0 | Y0 | D-0-11 |
| Nurek | 40 | 40 | 40 | 230 | 38.5 | 6.6 | 12.4 | 10.1 | 0.54 | 201.5 | 237.1 | 177 | 0.54 | 62.1 | 3 | 1 | 12 | 12 | Y0 | Y0 | D-0-11 |
|  | 40 | 40 | 40 | 230 | 38.5 | 6.6 | 12.4 | 22.73 | 9.76 | 202.3 | 202.3 | 173.9 | 0.56 | 58.5 | 3 | 1 | 12 | 12 | Y0 | Y0 | D-0-11 |
| Khujand | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 22.73 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Kanibadam | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.7 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Asht | 125 | 125 | 63 | 230 | 121 | 6.6 | 20.3 | 42.7 | 28.4 | 315 | 280 | 277 | 0.4 | 65 | 1 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 6.6 | 11 | 43.9 | 28.4 | 315 | 280 | 277 | 0.4 | 65 | 1 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Uzlovaya | 200 | 200 | 80 | 230 | 121 | 11 | 11 | 43.9 | 20 | 430 | 360 | 320 | 0.5 | 125 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 90 | 90 | 47 | 230 | 121 | 11 | 11 | 32 | 17.4 | 322 | 286 | 254 | 1.2 | 122 | 1 | 2.5 | 2 | 2 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 10.5 | 9.16 | 28.5 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Buston | 63 | 63 | 32 | 230 | 121 | 10.5 | 11.03 | 22.3 | 20.95 | 154.1 | 192.4 | 160.3 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y | Auto | D-0-11 |
|  | 32 | 32 | 16 | 230 | 121 | 11 | 11 | 34 | 21 | 163 | 145 | 128 | 0.6 | 32 | 3 | 2 | 6 | 6 | Y | Auto | D-0-11 |
| КNS-2 | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 34 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
|  | 125 | 125 | 63 | 230 | 121 | 10.5 | 20.3 | 42.3 | 30.3 | 315 | 280 | 277 | 0.4 | 65 | 3 | 2 | 6 | 6 | Y0 | Auto | D-0-11 |
| Rudaki | 63 | 63 | 32 | 230 | 121 | 10.5 | 11.03 | 34.1 | 20.96 | 157.1 | 192.4 | 160.29 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y | Auto | D-0-11 |
|  | 63 | 63 | 32 | 230 | 121 | 10.5 | 11.03 | 34.1 | 20.96 | 157.1 | 192.4 | 160.29 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y | Auto | D-0-11 |
| КNS-1 | 40 | --- | --- | 230 | - | 11 | 21.2 | --- | --- | 170 | --- | --- | 0.6 | 50 | 1 | 1.5 | 8 | 8 | Y/D-D-11-11 |  |  |
|  | 40 | --- | --- | 230 | - | 11 | 21.2 | --- | --- | 170 | --- | --- | 0.6 | 50 | 1 | 1.5 | 8 | 8 | Y/D-D-11-11 |  |  |
| Shahristan | 25 | - | 25 | 230 | - | 11 | 12,4 |  |  | 130 |  |  | 1 | 53 |  |  |  |  | Y | / | D |
| Aini | 63 | 63 | 32 | 230 | 121 | 10.5 | 11.03 | 22.3 | 20.95 | 154.1 | 192.4 | 160.3 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y | Auto | D-0-11 |
|  | 63 | 63 | 32 | 230 | 121 | 10.5 | 11.03 | 22.3 | 20.95 | 154.1 | 192.4 | 160.3 | 0.15 | 33.9 | 3 | 1.5 | 8 | 8 | Y | Auto | D-0-11 |
| Toj China | 18 | - | 18 | 230 | - | 11 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |