THE COMMITTEE FOR ARCHTECTURE AND CONSTRUCTION UNDER THE GOVERNMENT OF THE REPUBLIC OF TADJIKISTAN

GIINTIZ OJSC

Restricted

Copy_____

Archive No. 12319

Contract No. 9239

##### PRELIMINARY OPINION

ON ENGINEERING AND GEOLOGICAL RESEARCH FOR THE FACILITY

“Zeriistgokhi Basrkii “Convertori” bo iktodori 1300 MW dar doirai loikhai baini mintakavii CASA-1000”

(«Зериистгоҳи  Барќии «Конвертори» бо иќтидори 1300 мВт дар доираи лоихаи байни минтаќавии  САSА-1000»)

(Detailed Design stage)

#### Director 				Saidov R.S.

Head of Engineering Department 					Shonazarov B.F.

Chief Geologist 								Muinov R.R.

City of Dushanbe - 2016 г.

-2-

Geotechnical conditions of the site

Location

The project construction site is located on the territory of Sangtuda Jamoat, Dangarinsky district, 5.2 km to the south of Sangtuda-Dangara road junction, on the left side of the motor road Kurgan-Tube - Sangtuda.

The site is bounded by a wasteland from the north and south; by Kurgan-Tube - Sangtuda motor road - from the east, any by adyrs - from the west.

Geomorphological conditions

In terms of geomorphology the project construction site is confined to adyr portion of the foothill slopes. The relief is hilly. As at the time of survey the site was free from any developments.

Geological structure, hydrogeological conditions, physical and geological processes and phenomena

Deposits of deluvial-proluvial genesis, modern and Middle Quaternary age, represented by a layer of clay soils of more than 4.0 m thick contribute to the geological structure of the block.

The surface of the clay soils are covered with a layer of soil and vegetation of thickness up to 0.30 m. Penetrated thickness of deposits is 4.0 m; according to the archive materials, the total thickness of clay deposits exceeds 20.0 m.

In terms of the hydrogeology, a site surveyed is characterized by absence of underground water up to the depth of 4.0 m (according to archive materials, archive No. 96320, underground waters occur at a depth below 20.0 m, which eliminates its influence on the foundation soil.

Today’s physical and geological processes and phenomena on the block and adjacent territory are demonstrated in the form of gullies and mud flows during heavy rains and in spring.

Physical and Mechanical Properties of Soils

Engineering and geological elements within the active zone of soils of base foundation and soil base and their entire explored depth have been selected on the basis of analysis of spatial variability of certain indicators of soil properties measured by the laboratory methods, given the data on geological and lithological structure and hydrogeological conditions, in accordance with GOST 20522-96 and documents for internal use clarifying and explaining the said Standard.

As a result of estimates in the geological and lithological section 2 engineering-geological elements (EGE), have been selected, which are described below

Engineering and geological element 1 is represented by a soil and vegetation bed of 0.30 m thickness.

The standard density value is 1.20 t/m³.

Engineering and geological element No. 2, in terms of the standard index of plasticity of 0.062, is presented by sandy loam from of the color varying from pale brown to brownish, of medium density, macroporous – with pore diameter of 1-2 mm, of argillaceous texture, cloddy structure, hard texture.

The main characteristics of the physical and mechanical properties of EGE No.2 are presented by the following indicators:

-	Moisture content varies from 0.088 to 0.155 with standard value being 0.127 fraction units;

-	Porosity ratio varies from 0.716 to 0.956 fraction unit, with a standard value being 0.846;

-	Soil density in its natural state is 1.52 - 1.69 t/m³ with a standard value being 1.63 t/m3, the estimated value at the confidence factor is 0.95 -1.61 and 0.85 t/m3;

-	soil density in water-saturated condition is 1.84-1.97 t/m3, with a standard value being 1.90 t/m3, estimated value at the confidence factor of 0.95 is 1.88 t/m3, and at the confidence factor of 0.85 - 1.90 t/m3;

Deformation properties of clay soil were determined in the laboratory using the compression devices within the range of loads Rbyt + 0.2 MPa under its natural moisture content and water saturation.

Modulus of deformation in the natural state is 12.5-21.3 MPa, with a standard value being 17.1 MPa; in the water-saturated condition it is 2.0 -2.4 MPa, with a standard value being 2.2 MPa.

The strength characteristics of EGE No. 2 have been determined in the laboratory by method of nonconsolidated cut with its water saturation in the range of loads of  0.1-0.3 MPa and are as follows:

- adherence - 0.0075-0.0100 MPa, with a standard value being 0.0083 MPa, the estimated value at the confidence factor of 0.95 is 0.0075 MPa and at the confidence factor of 0.85 - 0.0080 MPa.

- Angle of internal friction of 22º10 '- 24º30', with a normative value being 24º00', the estimated value at the confidence ratio of 0.95 is 23º05', and at the confidence ratio of 0.85 - 23º 45'(appendices Nos.1, 2).

Clay soils of the block have subsiding properties both under the natural pressure and additional loads. The relative subsidence at Rbyt is 0.012 - 0.022 MPa, and with the loads of Rbyt. + final load they increase up to 0.052. Subsiding properties of soils occur at the interval of depths of 0.30-4.0 m. The value of the initial subsidence pressure is 0.010-0.063 MPa, with a standard value being 0.031-0.042. The subsidence value at Rbyt. is 5.8-6.8 cm, per explored thickness of subsidence depth of 3.7 m. The total value of subsidence over the entire subsidence thickness can reach 20-25 cm (according to archive materials). Type of soil conditions for manifestation of subsidence properties is II (second) (Appendix 3).

Clay soils of the block were compacted in the laboratory using the method described in GOST 22733-2002; after 40 beats on the compaction device the maximum density of dry (skeleton) soil of was 1.66-1.67 t/m3 with the optimum moisture content 0.180 - 0.186 fraction units (Appendix No. 4).

Corrosiveness of clay soils in relation to carbon steel and low alloy steel is average (Appendix No.5).

Corrosiveness of clay soils in relation to the non-ferrous metals: aluminium cover of cable is high; to lead cladding is therefore, while designing it is necessary to provide for the measures for corrosion protection of engineering communications (Appendix No.6).

According to the chemical composition, in terms of the content of SO4 clay soils of the block are lightly aggressive to Portland cements according to GOST 10178-85 for all brands of cement on terms of waterproofing (Appendix No. 7);

- in terms of CL content, with due account of SO4, the soils of the block are medium-aggressive to the fixtures of reinforced concrete structures on all brands of cement (Appendix No.7).

Soils of the block are non-saline, and content of plant fragments does not exceed the permissible norms (Appendix No. 8).

Building category of soils in terms of its workout should be accepted according to ESN RT-2007-01, Table 1, pp 9 b), 36 c), depending on the type of development and type of mechanisms applied.

The steepness of slopes of pits and trenches is accepted in accordance with MҚS ChT 50-01-2007, table 13.1, page 156, and depending on the depth of its digging and nomenclature of soils, the steepness will have the following values:

| Soil | ### At the depth of digging, in meters, up to |  |  |
| --- | --- | --- | --- |
|  | 1.5 | 3.0 | 5.0 |
| Sand clay | 1: 0.25 | 1: 0.67 | 1: 0.8 |

Note: at a pit depth of more than 5.0 m, the steepness of slopes is determined according to the calculation.

Arrangements in accordance with KS 50-01-2007, pp 3.68-3.71, i.e. construction of soil bed of local materials and increasing density of its skeleton  up to 1.67 t/m3, with optimum moisture content of soil being 0.180 - 0.186 fraction units, are recommended as a method of engineering preparation of the foundation of  the designed building.

Given the development of the physical and geological processes on the block of the planned construction, the following measures should be taken during construction:  designing, construction should be made direct to the implementation of the following measures;

-	Filling of all existing gullies with clay soil with ramming;

-	Harvesting and removal of atmospheric precipitations;

-	Engineering communications should be laid in accordance with the requirements of constructions norms for subsiding soils ΙI of (second) type.

-	Step of height of more than 3.0 m, formed during the planning work should be reinforced by retaining walls.

Seismic activity on the block, according to the seismic zoning map of the territory of the Republic of Tajikistan is assessed at 7 points.

Prepared by 					Morkel N.V.

Chief Geologist 				Muinov R.R.

GIINTIZ OJSC                                                                                                                                                                                  Appendix No. 1

Sheet 1

Arch. № 12319

TABLE OF PHYSICAL AND MECAHICAL PROPERTIES OF SOILS

Facility: “Zeriistgokhi Basrkii “Convertori” bo iktodori 1300 MW dar doirai loikhai baini mintakavii CASA-1000”

| Seq. No. | Pit No. | Depth, m | Specific weight | Density t/m3 |  |  |  | Soil porosity | Soil porosity ratio |  |  | Soil moisture in fraction units |  |  |  |  | index of plasticity | Soil type |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | In natural condition | Under full saturation | Suspended | Skeleton |  | Under natural moisture content | With moisture content at liquid limit |  | Natural | Moisture level under natural conditions | Maximum water capacity | At liquid level | At limit of plasticity |  |  | № EGE |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
|  |  |  | rs | r | rв | rв | rd | n | е | еL | W |  | Iw | Wп | WL | Wp | Jp |  |  |
| 1 | Pit -1 | 2.0 | 2.66 | 1.56 | 1.89 | 0.89 | 1.42 | 0.466 | 0.873 | 0.761 | 0.098 |  | 0.30 | 0.328 | 0.286 | 0.221 | 0.065 | Sand clay | 2 |
| 2 | -//- | 4.0 | 2.66 | 1.64 | 1.84 | 0.84 | 1.43 | 0.462 | 0.860 | 0.638 | 0.143 |  | 0.44 | 0.323 | 0.240 | 0.171 | 0.069 | Sand clay | 2 |
| 3 | Pit -2 | 2.0 | 2.66 | 1.69 | 1.97 | 0.97 | 1.55 | 0.417 | 0.716 | 0.849 | 0.089 |  | 0.33 | 0.269 | 0.319 | 0.252 | 0.067 | Sand clay | 2 |
| 4 | -//- | 4.0 | 2.66 | 1.68 | 1.92 | 0.92 | 1.48 | 0.444 | 0.797 | 0.774 | 0.135 |  | 0.45 | 0.300 | 0.291 | 0.231 | 0.060 | Sand clay | 2 |
| 5 | Pit -3 | 2.0 | 2.66 | 1.62 | 1.91 | 0.91 | 1.45 | 0.455 | 0.834 | 0.777 | 0.120 |  | 0.38 | 0.314 | 0.292 | 0.230 | 0.062 | Sand clay | 2 |
| 6 | -//- | 4.0 | 2.66 | 1.65 | 1.90 | 0.90 | 1.44 | 0.459 | 0.847 | 0.740 | 0.146 |  | 0.46 | 0.319 | 0.278 | 0.213 | 0.065 | Sand clay | 2 |
| 7 | Pit -4 | 2.0 | 2.66 | 1.52 | 1.87 | 0.87 | 1.39 | 0.477 | 0.914 | 0.737 | 0.103 |  | 0.30 | 0.343 | 0.277 | 0.224 | 0.053 | Sand clay | 2 |
| 8 | -//- | 4.0 | 2.66 | 1.60 | 1.90 | 0.90 | 1.40 | 0.504 | 0.900 | 0.779 | 0.136 |  | 0.38 | 0.360 | 0.293 | 0.234 | 0.059 | Sand clay | 2 |
| 9 | Pit -5 | 2.0 | 2.66 | 1.68 | 1.96 | 0.96 | 1.54 | 0.421 | 0.727 | 0.747 | 0.088 |  | 0.32 | 0.273 | 0.281 | 0.212 | 0.069 | Sand clay | 2 |
| 10 | -//- | 4.0 | 2.66 | 1.65 | 1.91 | 0.91 | 1.45 | 0.455 | 0.834 | 0.742 | 0.139 |  | 0.44 | 0.314 | 0.279 | 0.213 | 0.066 | Sand clay | 2 |

GIINTIZ OJSC                                                                                                                                                                                       Appendix No.1

Sheet 2

Arch. № 12319

TABLE OF PHYSICAL AND MECAHICAL PROPERTIES OF SOILS

| Seq. No. | Coefficient |  |  |  |  | Modulus of deformation. |  | Natural pressure value, MPa |  | Relative subsidence |  |  |  |  |  | Initial subsidence pressure MPa | Internal friction angle 0 |  | Adherence, MPa |  | Texture |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Compaction under natural condition | Compaction under water-saturated condition | Depending on the soil lateral expansion | Working conditions under natural condition | Working conditions under water-saturated condition | Under natural conditions MPa | Under water-saturated condition, MPa |  |  | Under natural pressure. MPa | Under load Rbyr,. + 0.05 MPa | Under load Rbyt + 0.1 MPa | Under load Rbyt. + 0.15 MPa | Under load Rbyt. + 0.2 MPa | Under load Rbyt. + 0.25 MPa |  | Under natural condition 0 | Under water-saturated condition, 0 | В Under natural condition., MPa | Under water-saturated condition MPa | Under natural condition | Under water-saturated condition |
|  | а | аw | b | m | mw | E | Ew | Рn |  |  |  |  |  |  |  | Рps | j | jw | С | Сw | JL | JL |
|  | 19 | 20 | 21 | 24 | 25 | 26 | 27 | 28 |  | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | <0 | 1.65 |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | <0 | 2.20 |
| 3 | 0.15 | 0.57 | 0.664 | 2.0 | 1.0 | 15.2 | 2.0 | 0.039 | 0.019 |  | 0.021 | 0.031 | 0.042 | 0049 |  | 0.021 |  | 24º15´ |  | 0.0075 | <0 | 0.25 |
| 4 | 0.13 | 0.53 | 0.676 | 2.0 | 1.0 | 19.3 | 2.3 | 0.077 | 0.015 |  | 0.018 | 0.025 |  |  |  | 0.051 |  |  |  |  | <0 | 1.15 |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | <0 | 1.35 |
| 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | <0 | 1.63 |
| 7 | 0.21 | 0.66 | 0.687 | 2.0 | 1.0 | 12.5 | 2.0 | 0.037 | 0.018 |  | 0.023 | 0.035 | 0.048 | 0.052 |  | 0.021 |  | 22º30´ |  | 0.0100 | <0 | 2.24 |
| 8 | 0.12 | 0.54 | 0.677 | 2.0 | 1.0 | 21.0 | 2.4 | 0.076 | 0.012 |  | 0.020 | 0.023 |  |  |  | 0.063 |  |  |  |  | <0 | 2.14 |
| 9 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | <0 | 0.88 |
| 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | <0 | 1.53 |

GIINTIZ OJSC                                                                                                                                                                               Appendix No.1

Sheet 3

Arch. № 12319

TABLE OF PHYSICAL AND MECAHICAL PROPERTIES OF SOILS

| Seq. No. | Pit No. | Depth, m | Specific weight | Density, t/m3 |  |  |  | Soil porosity | Soil porosity ratio |  | Soil moisture content in fraction units |  |  |  |  | index of plasticity | Soil type |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | In natural condition | Under full saturation | Suspended | Skeleton |  | Under natural moisture content | № EGE | Natural | Moisture level under natural conditions | Maximum water capacity | At liquid level | At limit of plasticity |  |  | № ИГЭ |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
|  |  |  | rs | r | rв | rв | rd | n | е | еL | W | Iw | Wп | WL | Wp | Jp |  |  |
| 11 | Pit -6 | 2.0 | 2.66 | 1.69 | 1.93 | 0.93 | 1.49 | 0.440 | 0.785 | 0.761 | 0.134 | 0.45 | 0.295 | 0.286 | 0.219 | 0.067 | Sand clay | 2 |
| 12 | -//- | 4.0 | 2.66 | 1.65 | 1.90 | 0.90 | 1.44 | 0.459 | 0.847 | 0.689 | 0.146 | 0.46 | 0.319 | 0.259 | 0.202 | 0.057 | Sand clay | 2 |
| 13 | Pit-7 | 2.0 | 2.66 | 1.57 | 1.86 | 0.86 | 1.37 | 0.485 | 0.942 | 0.713 | 0.142 | 0.40 | 0.354 | 0.268 | 0.205 | 0.063 | Sand clay | 2 |
| 14 | -//- | 4.0 | 2.66 | 1.58 | 1.85 | 0.85 | 1.36 | 0.489 | 0.956 | 0.732 | 0.155 | 0.43 | 0.360 | 0.275 | 0.216 | 0.059 | Sand clay | 2 |
| 15 | Pit -8 | 2.0 | 2.66 | 1.57 | 1.87 | 0.87 | 1.40 | 0.474 | 0.900 | 0.747 | 0.118 | 0.35 | 0.339 | 0.281 | 0.219 | 0.062 | Sand clay | 2 |
| 16 | -//- | 4.0 | 2.66 | 1.67 | 1.92 | 0.92 | 1.48 | 0.444 | 0.797 | 0.692 | 0.132 | 0.44 | 0.300 | 0.260 | 0.205 | 0.055 | Sand clay | 2 |

GIINTIZ OJSC                                                                                                                                                                                Appendix No.1

Sheet 4

Arch. No. № 12319

TABLE OF PHYSICAL AND MECAHICAL PROPERTIES OF SOILS

| Seq.No. | Coefficient |  |  |  |  | Modulus of deformation |  | Natural pressure value, MPa | Relative subsidence |  |  |  |  |  | Initial subsidence pressure MPa | Internal friction angle 0 |  | Adherence, MPa |  |  | Texture |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Compaction under natural condition | Compaction under water-saturated condition | Depending on the soil lateral expansion | Working conditions under natural condition | Working conditions under water-saturated condition | Under natural conditions MPa | Under water-saturated condition, MPa |  | Under natural pressure. MPa | Under load Rbyr,. + 0.05 MPa | Under load Rbyt + 0.1 MPa | Under load Rbyt. + 0.15 MPa | Under load Rbyt. + 0.2 MPa | Under load Rbyt. + 0.25 MPa |  | Under natural condition 0 | Under water-saturated condition | В Under natural condition., MPa | Under water-saturated condition MPa | Under natural condition |  | Under water-saturated condition |
|  | а | аw | b | m | mw | E | Ew | Рn |  |  |  |  |  |  | Рps | j | jw | С | Сw |  | JL | JL |
|  | 19 | 20 | 21 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 |  | 40 | 41 |
| 11 | 0.15 | 0.56 | 0.664 | 2.0 | 1.0 | 16.0 | 2.1 | 0.019 | 0.020 | 0.022 | 0.035 | 0.049 |  |  | 0.010 |  | 22º 10´ |  | 0.0095 |  | <0 | 1.13 |
| 12 | 0.14 | 0.63 | 0.680 | 2.0 | 1.0 | 18.5 | 2.0 | 0.076 | 0.015 | 0.019 | 0.026 |  |  |  | 0.051 |  | 24º 10´ |  | 0.0075 |  | <0 | 2.05 |
| 13 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | <0 | 2.37 |
| 14 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | <0 | 2.44 |
| 15 | 0.19 | 0.61 | 0.672 | 2.0 | 1.0 | 13.2 | 2.1 | 0.037 | 0.022 | 0.028 | 0.035 | 0059 |  |  | 0.017 |  | 24º 10´ |  | 0.0075 |  | <0 | 1.94 |
| 16 | 0.12 | 0.53 | 0.683 | 2.0 | 1.0 | 21.3 | 2.3 | 0.077 | 0.013 | 0.020 | 0.025 |  |  |  | 0.059 |  | 24º 30´ |  | 0.0085 |  | <0 | 1.73 |

Prepared by                     Morkel N.

GIINTIZ OJSC                                                                                                                                                                               Appendix No.2

Sheet 1

Arch № 12319

RESULTS OF STATISTIC PROCESSING OF THE DATA OF SOIL CHARACTERISTICS

(normative vs estimated)

Engineering and geological element No.1 – soil and vegetation bed

Рнnat. = 1.20 t/m3

Engineering and geological element No. 2 - Jн = 0.062 – sand soil

(solid texture)

wн = 0.127      ен = 0.846                    Рнnat. = 1.63 т/м3                 Рнwat. .= 1.90 т/м3                         Eнnat   = 17.1  МПа

υ = 0.16         υ = 0.08                        υ = 0.03                                υ = 0.02                                         Eнwat =  2.2  МПа

pΙ = 1.61 т/м3                     pΙ = 1.88 т/м3

pΙΙ =1.61 т/м3                     pΙΙ = 1.90 т/м3

CY tcn  = 0/0083                φy nat/= 24º00’

υ  = 0.10                       υ = 0.01

СI   = 0.0075                    φI  =  23º05'

СII   = 0.0080                    φ II = 23º45'

Prepared by Morkel N

GIINTIZ OJSC                                                                                                                                                                                Appendix No.3

Sheet 1

Arch. № 12319

#### SUMMARY TABLE OF SOIL CONDITIONS IN TERMS OF SUBSIDENCE

Facility: “Zeriistgokhi Basrkii “Convertori” bo iktodori 1300 MW dar doirai loikhai baini mintakavii CASA-1000”

| Seq. No. | Nos. of pits | Depth of taking monoliths, meters | Depth interval of subsiding soils | Relative subsidence at Рbyt. | Relative subsidence. + additional load MPa | Subsidence at Rbyt, in cm | Thickness of subsidence depth at Rbyt. in meters | Thickness of subsidence depth at Rbyt + additional load in meters | Initial subsidence pressure MPa | Initial normative subsidence pressure MPa | Type of soil conditions |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Pit -2 | 2.0 | 0.30 – 2.5 | 0.019 | 0.049 | 4.2 | 2.2 | 2.2 | 0.021 |  |  |
| 2 | -//- | 4.0 | 2.5 – 4.0 | 0.015 | 0.025 | 2.3 | 1.5 | 1.5 | 0.051 |  |  |
|  |  |  |  |  |  | 6.5 cm | 3.7 м | 3.7 м |  | 0.036 | II (second) |
| 3 | Pit -4 | 2.0 | 0.30 – 2.5 | 0.018 | 0.052 | 4.0 | 2.2 | 2.2 | 0.021 |  |  |
| 4 | -//- | 4.0 | 2.5 – 4.0 | 0.012 | 0.023 | 1.8 | 1.5 | 1.5 | 0.063 |  |  |
|  |  |  |  |  |  | 5.8 cm | 3.7 м | 3.7 м |  | 0.042 | II (second) |
| 5 | Pit -6 | 2.0 | 0.30 – 2.5 | 0.020 | 0.049 | 4.4 | 2.2 | 2.2 | 0.010 |  |  |
| 6 | -//- | 4.0 | 2.5 – 4.0 | 0.015 | 0.026 | 2.3 | 1.5 | 1.5 | 0.051 |  |  |
|  |  |  |  |  |  | 6.7 cm | 3.7 м | 3.7 м |  | 0.031 | II (second) |
| 7 | Pit -8 | 2.0 | 0.30 – 2.5 | 0.022 | 0.050 | 4.8 | 2.2 | 2.2 | 0.017 |  |  |
| 8 | -//- | 4.0 | 2.5 – 4.0 | 0.013 | 0.025 | 2.0 | 1.5 | 1.5 | 0.059 |  |  |
|  |  |  |  |  |  | 6.8 cm | 3.7 м | 3.7 м |  | 0.038 | II (second) |

Prepared by Morkel N.

GIINTIZ OJSC

Appendix No. 4

Sheet 1

Arch. № 12319

# RESULTS

of soil compaction at the laboratory

Facility: “Zeriistgokhi Basrkii “Convertori” bo iktodori 1300 MW dar doirai loikhai baini mintakavii CASA-1000”

| Seq. No. | Pit, well and its No. | Depth, meters | Density t/m3 |  | Soil moisture in unit fraction W |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Of soil Р | Of soil skeleton. р |  |
| 1 | 2 | 3 | 4 | 5 | 6 |
| 1. | Pit -2 | 2.0 | 1.86 | 1.64 | 0.135 |
| 2. |  |  | 1.91 | 1.66 | 0.153 |
| 3. |  |  | 1.96 | 1.67 | 0.171 |
| 4. |  |  | 2.00 | 1.65 | 0.169 |
| 5. |  |  | 1.97 | 1.67 | 0.186 |
| 6. | Pit -6 | 4.0 | 1.85 | 1.64 | 0.125 |
| 7. |  |  | 1.91 | 1.66 | 0.148 |
| 8. |  |  | 1.94 | 1.65 | 0.167 |
| 9. |  |  | 1.98 | 1.66 | 0.180 |
|  |  |  | 1.98 | 1.63 | 0.214 |

Geotechnics laboratory assistant				Ziyadullayev G.

GIINTIZ OJSC                                                                                            Appendix No.5

Sheet 1

Arch. № 12319

RESULTS OF ANALYSIS OF CORROSIVENESS OF SOILS

USING SPECIFIC RESISTANCE METHOD

Facility: “Zeriistgokhi Basrkii “Convertori” bo iktodori 1300 MW dar doirai loikhai baini mintakavii CASA-1000”

| Seq. No. | Pit No. | Depth of taking, m | SR on Omh.m | Soil corrosiveness |
| --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 |
| 1 | Pit – 1 | 1.0 | 29.61 | Medium |
| 2 | Pit – 2 | 2.0 | 25.67 | Medium |
| 3 | Pit – 3 | 1.0 | 27.13 | Medium |
| 4 | Pit – 4 | 2.0 | 31.38 | Medium |
| 5 | Pit – 5 | 1.0 | 30.10 | Medium |
| 6 | Pit – 6 | 2.0 | 20.18 | Medium |
| 7 | Pit – 7 | 1.0 | 22.15 | Medium |
| 8 | Pit– 8 | 2.0 | 23.05 | Medium |

Geotechnics laboratory assistant				Ziyadullayev G.

GIINTIZ OJSC                                                                                            Appendix No. 6

Sheet 1

Arch. № 12319

RESULTS OF ANALYSIS OF CORROSIVENESS OF SOILS TO NON-FERROUS METALS

Facility: “Zeriistgokhi Basrkii “Convertori” bo iktodori 1300 MW dar doirai loikhai baini mintakavii CASA-1000”

| Seq. No. | Pit No. | Depth of taking, m | РН | Chlorine-ions, % СL | Nitrate ions, % NОз | Iron ions, % Fe | Organic substances, % |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| 1 | Pit – 1 | 1.0 | 6.8 | 0.0053 | 0.0005 | No | 0.0052 |
| 2 | Pit – 2 | 2.0 | 7.0 | 0.0062 | 0.0003 | no | 0.0056 |
| 3 | Pit – 3 | 1.0 | 7.0 | 0.0072 | 0.0007 | no | 0.0063 |
| 4 | Pit – 4 | 2.0 | 7.0 | 0.0057 | 0.0008 | no | 0.0061 |
| 5 | Pit – 5 | 1.0 | 6.9 | 0.0059 | 0.0008 | no | 0.0068 |
| 6 | Pit – 6 | 2.0 | 7.1 | 0.0063 | 0.0009 | no | 0.0063 |
| 7 | Pit – 7 | 1.0 | 7.2 | 0.0060 | 0.0005 | no | 0.0068 |
| 8 | Pit – 8 | 2.0 | 7.3 | 0.0077 | 0.0008 | no | 0.0075 |

Analyst				Dadabayeva G.

GIINTIZ OJSC                                                                                                                                                                         Appendix No. 7

Sheet 1

Arch. № 12319

# TABLE

of chemical composition of soils

(type of analysis: water extract)

Facility:« “Zeriistgokhi Basrkii “Convertori” bo iktodori 1300 MW dar doirai loikhai baini mintakavii CASA-1000”

| Seq. No. | Pit No. | Depth, in meters | Mg/kg of soil |  |  |  |  |  |  |  | PH | Mg equivalent |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Dry residue | alkalinity |  | Cℓ' | SO4" | Ca" | Mg" | Na'+K' |  | alkalinity |  | Cℓ' | SO4" | Ca" | Mg" | Na'+K' |
|  |  |  |  | СО3" | НСО'3 |  |  |  |  |  |  | СО3" | НСО'3 |  |  |  |  |  |
| 1. | Pit - 1 | 1.0 | 2895.0 | No | 213 | 583 | 934 | 1022 | 72 | 71 | 6.8 | No | 0.35 | 1.64 | 4.02 | 5.10 | 0.60 | 0.31 |
| 2. | Pit - 2 | 2.0 | 3149.0 | No | 225 | 617 | 850 | 1322 | 108 | 27 | 7.0 | No | 0.37 | 1.74 | 5.51 | 6.60 | 0.90 | 0.12 |
| 3. | Pit - 3 | 1.0 | 2554.0 | No | 183 | 480 | 920 | 861 | 60 | 50 | 7.0 | No | 0.30 | 1.35 | 3.97 | 4.30 | 0.50 | 0.22 |
| 4. | Pit - 4 | 2.0 | 2849.0 | No | 210 | 580 | 900 | 1020 | 70 | 69 | 7.0 | No | 0.32 | 1.60 | 4.00 | 5.00 | 0.62 | 0.30 |
| 5. | Pit - 5 | 1.0 | 2986.0 | No | 210 | 560 | 850 | 1221 | 70 | 75 | 6.9 | No | 0.30 | 1.62 | 4.03 | 5.12 | 0.62 | 0.15 |
| 6. | Pit - 6 | 2.0 | 3077.0 | No | 230 | 620 | 890 | 1200 | 107 | 30 | 7.1 | No | 0.33 | 1.70 | 5.42 | 6.20 | 0.70 | 0.0 2 |
| 7. | Pit - 7 | 1.0 | 2964.0 | No | 180 | 450 | 905 | 1310 | 64 | 55 | 7.2 | No | 0.32 | 1.45 | 3.39 | 4.50 | 0.60 | 0.25 |
| 8. | Pit - 8 | 2.0 | 3032.0 | No | 200 | 530 | 920 | 1242 | 75 | 65 | 7.3 | No | 0.35 | 1.52 | 4.10 | 5.03 | 0.65 | 0.32 |

Analyst				Dadabayeva G.