## BoQ_CASA1000
Annexure B
Bill of Quantity (BOQ)
Supply & Installation of Bi-Pole Sangtuda-Nowshera HVDC Package associated with CASA 1000
Sl. No. |  | Item Description | Unit | QTY | QTY
|  |  |  | Package 1 LOT 1 Tajikistan Sangtuda | Package 1 LOT 2 Pakistan Nowshera
A) | HVDC CONVERTER EQUIPMENT
| 1a | Thyristor Valves(Quad) with specified ratings | Quadruple Valve | 6 | 6
| 1b | Valve hall equipment, Hardware and Surge Arrester (one set of each valve hall) | LOT | 2 | 2
| 2A | Converter Transformers ( Single Phase three wdg.) | Nos. | 6 | 6
| 3 | Control, Protection and SCADA
| 3a) | Control Protection and SCADA for HVDC System | LOT | 1 | 1
| 4 | Smoothing Reactor ,Pole (HV) & neutral (LV) bus | LOT | 1 | 1
| 5 | DC Filters equipments | SET | 2 | 2
| 6 | DC CT | LOT | 1 | 1
| 7 | DC Voltage Divider | LOT | 1 | 1
| 8 | Other DC Switchyard Equipment
| 8.1 | Pole bus | LOT | 1 | 1
| 8.2 | Neutral bus | LOT | 1 | 1
| 8.3 | Disconnectors & grounding switches | LOT | 1 | 1
| 8.4 | DC Arresters | LOT | 1 | 1
| 8.5 | Wall Bushings | LOT | 1 | 1
| 8.6 | Bus support Insulator for DC switchyard | LOT | 1 | 1
| 8.7 | Erection Hardware for DC switchyard | LOT | 1 | 1
| 9 | Communication Equipment
| 9( a) | Back up Communication, PLCC including repeater station if any | LOT | 1 | 1
| 10) | Computer Program/Software | LOT | 1 | 1
| 11 | All Necessary equipments for Earth Electrode Station | LOT | 1 | 1
B) | AC SWITCHYARD EQUIPMENT
| 1 | Transformer
| 1.a | 167 MVA , 500KV/220 KV single phase Auto transformer | No. | 4 | -
| 1.b | LT Transformer
| 1.b.i | 30/20/0.415 kV Station Auxiliary Transformer | No. | 4 | 4
| 1.b.ii | Auxiliary Transformer (for DC Line charging) | No. | 2 | 2
| 2 | 500 kV Equipment
| 2.1 | 500 kV AC Filter Equipment (Sub-Bank) including its EHV Switchgear ( CB, Isol, CT etc. ); | LOT | LOT | LOT
| 2.2 | 550 kV AC Circuit Breakers (3 phase unit)
| 2.2.1 | 3150 A Converter Breaker with Point on Wave switching | Nos. | 8 | 6
| 2.2.2 | 3150 A Line side/ Transformer bay Breaker with PIR Switching | Nos. | 3 | 3
| 3 | 550 kV Current Transformers(1ph unit )
| 3.1 | 3000 A, 40 kA CT with 120% extended current rating | Nos. | 33 | 30
| 4 | 550 kV Capacitive Voltage Transformer, 8800/6600/4400 pF (as applicable), 1-phase | Nos. | 9 | 6
| 4.1 | CVT/Inductive PT for Valve Timing | LOT | LOT | LOT
| 4.2 | 550 kV Bus Pot Insulators | LOT | LOT | LOT
| 5 | 550 kV Isolators
| 5.1 | 3150/2000A with 2 E/s (as applicable) | LOT | LOT | LOT
| 5.2 | 3150/2000A with 1 E/s (as applicable) | LOT | LOT | LOT
| 6 | 444 kV Gapless Surge Arrester (1-phase) | Nos. | 6 | NA
| 6.1 | 444 kV Gapless Surge Arrester( 1 Phase) for filter bus | Nos. | 9 | 6
| 6.2 | 444 kV Gapless Surge Arrestor( 1 Phase) as per Chapter 1, Clause No 1.2.1 (b) | Nos | 9 | 9
| 7 | AC Bus Bar equipment with all accessories, fittings, fixure etc. as applicable | LOT | LOT | LOT
| 8 | PLC Filters equipment | LOT | LOT | LOT
| 9. | PLCC
| 9.1 | Line Traps
| 9.1.1 | 3150A,500 kV 0.5 mH, 40 kA | Nos. | 2 | NA
| 9.1.2 | BPI for the above | Nos. | 6 | NA
| 9.1.3 | Coupling device (phase to phase) | Set | 1 | NA
| 9.1.4 | HF cable | LS | 1 | NA
| 9.1.5 | Carrier Equipment (for speech+protection and for speech+Data) | Nos. | 4 | NA
| 9.1.6 | Protection Coupler | Nos. | 2 | NA
| 9.1.7 | EPAX (24/8) with 24 telephones, cables etc. | Set | 2 | 2
| 9.1.8 | EPAX (4/4) with 4 telephones, cables etc. | Set | 2 | NA
| 9.1.9 | Testing & Maintenance equipment( As per specification) | Set | 1 | 1
| 9.1.10 | PLCC Repeater stations | Set | As required | As required
| 10.1 | Energy Meter main as per Technical Specification for AC lines (At Nowshera for Tarbela Sheikh and Sheikh Muhamadi) | Set | 2 | 4
| 10.2 | Energy Meter check as per Technical Specification for AC lines (At for Tarbela Sheikh and Sheikh Muhamadi) | Set | 2 | 4
| 10.3 | Emergency Control Device (ECD)
| 10.3.i | Fixation of line tripping (FTL) | Nos. | 1+1 | NA
| 10.3.ii | Automatic Interruption of out of step operation main and standby sets (AIOO) | Nos. | 1+1 | NA
| 10.3.iii | Automatic fixing of active power overload by current metering (AFPO) | Nos. | 1+1 | NA
| 11. | Erection Hardware
| 11.1 | Bus Post Insulators & Insulator strings, Disc Insulators, Hardware, Spacers, conductor(s), bus-bar material, cable trays, Bay MB, clamps, connectors including equipment connectors, junction box, earthwire, earthing material, risers, auxiliary earthmat (excluding main earthmat), buried/RCC cable trenches/pipes for equipment & lighting, all accessories etc. for the following | LOT | LOT | LOT
| 12. | 500kV D-type layout
| 12.1 | Line bay (*For connecting Nowshera C89 Converter Station to 500 kV NTDC Station) | Set | 1 | 2*
| 12.2 | Transformer bay | Set | 1 | NA
| 12.3 | Spare bay of half dia. | Set | 1 | NA
| 12.4 | Bus (One and half breaker scheme) | Set | 1 | 1
| 13 | 220 kV Equipment
| 13.1 | 245 kV Circuit Breaker (3 phase) with support structure
| 13.1.a | 1600 A, 31.5 kA | Set | 4 (including DMT at remote end) | NA
| 13.1.b | 2500 A, 31.5 kA | Set | 1 | NA
| 14 | 245 kV Current Transformer
| 14.1 | 1600 A, 31.5 kA with 120% extended current rating | Nos. | 12(including CT for remote end) | NA
| 14.2 | 2500 A, 31.5 kA with 120% extended current rating | Nos. | 3 | NA
| 15 | 245 kV Capacitive Voltage Transformer (1-Phase)
| 15.1 | 4400pF | Nos. | 12 | NA
| 16 | 245 kV Isolator (3-phase) double break
| 16.1 | 1600A, 31.5 kA, Isolator with one E/S | Nos. | 4 | NA
| 16.2 | 1600A, 31.5 kA, Isolator with two E/S | Nos. | 4 | NA
| 16.3 | Tandem Isolator without earth switch |  | 7 | NA
| 16.4 | 2500A, 31.5 kA, Isolator with two E/S | Nos. | 2 | NA
| 17 | 198 kV Surge Arrester (1- Phase) | Nos. | 6+3 | NA
| 17(a) | 198 kV Surge Arrester (1- Phase) as per Chapter 1 Clause 1.2.1 (b) | Nos | 9 | 9
| 18 | 245 kV Bus Post Insulator | LOT | LOT | NA
| 19 | AC Bus Bar equipment with all accessories, fittings, fixure etc.( as applicable) | LOT | LOT | NA
| 20 (a) | Digital PLCC (220 kV)
| 20.1.6 | Digital Protection Coupler | Nos. | 1+1 | NA
| 20(b) | Fibre optical terminal equipment (220 kV) | LOT | LOT 1 | NA
| 21.1 | Energy Meter main as per Technical Specification for AC lines | Set | 1+1 | NA
| 21.2 | Energy Meter check as per Technical Specification for AC lines | Set | 1+1 | NA
| 22 | Erection Hardware (220 kV)
|  | Bus Post Insulators & Insulator strings, Disc Insulators, Hardware, Spacers, conductor(s), bus-bar material, cable trays, Bay MB, clamps, connectors including equipment connectors, junction box, earthwire, earthing material, risers, auxiliary earthmat (excluding main earthmat), buried/RCC cable trenches/pipes for equipment & lighting, all accessories etc. for the following | LOT | LOT | NA
| 23 | 220 kV DMT Scheme layout (Sangtuda)
| 23.1 | Line Bay | Set | 1 | NA
| 23.2 | Transformer Bay | Set | 1 | NA
| 23.3 | Bus (DMT) | Set | 1 | NA
| 23.4 | Transfer Bus Coupler Bay | Set | 1 | NA
| 23.5 | Bus Coupler bay | Set | 1 | NA
| 24 | 33/20 kV EQUIPMENT
| 24.1 | 33/20 kV Circuit breaker | LOT | LOT | LOT
| 24.2 | 33/20 kV Isolator ( For LT Transformer as applicable)
| 24.2.1 | With one E/s | LOT | LOT | LOT
| 24.2.2 | With two E/S | LOT | LOT | LOT
| 24.2.3 | Without E/s | LOT | LOT | LOT
| 24.3 | 33/20 kV Current Transformer | LOT | LOT | LOT
| 24.4 | 33/20 Horn Gap fuse ( For LT Transformer as applicable) | LOT | LOT | LOT
| 24.5 | Surge Arrestors (Gapless)
| 24.5.1 | 33 kV | LOT | NA | LOT
| 24.5.2 | 20 kV | LOT | LOT | NA
| 25 | Control & Relay Panels
| 25.1 | 500 kV (Simplex type panels)
| 25.1.1 | Circuit Breaker Relay Panel
| 25.1.1.a | With Auto Reclose | Nos. | 2 | NA
| 25.1.1.b | With out Auto Reclose | Nos. | 9 | 9
| 25.1.2 | Line Protection Panel *= Protection panel for NTDC feeder | Nos. | 1 | 1*
| 25.1.3 | Transformer Protection Panel (For both HV & MV side) | Nos. | 1 | NA
| 25.1.4 | Numerical Bus Bar Protection Panel (500 kV Duplicated bus bar protection) | Set | 1 | 1
| 25.2 | 220 kV (Simplex type panels)
| 25.2.1 | Circuit Breaker Relay Panel
| 25.2.1.1 | With Auto Reclose | Nos. | 1+1 | NA
| 25.2.1.2 | With out Auto Reclose | Nos. | 3 | NA
| 25.2.2 | Line Protection Panel | Nos. | 1+1 | NA
| 25.2.3 | Transformer Protection Panel (For both HV & MV side) | Nos. | 1 | NA
| 25.2.4 | Bus Bar Protection Panel 220kV (Duplicate bus bar protection) | LS | 1 | NA
| 25.2.5 | Augmentation of existing bus bar protection scheme | LS | 1 | NA
| 25.3 | Other/common equipments pertaining to C&R system
| (i) | Event Logger | No. | 1 | 1
| (ii) | Common Equipment (Voltage, Frequency recorder, Digital voltage and frquency meters for 500kV & 220KV system) | Set | 1 | 1
| (iii) | Synchronising Trolley | No. | 1 | NA
| (iv) | Time synchronisation equipment | No. | 1 | 1
| (v) | Special Relay Test kit | No. | 1 | NA
| 25.4 | Substation automation system for 500kV &220kV s/s including hardware and software for remote control station alongwith associated civil works for bay controller rooms for following bays: 500kV Bays - As per scope 220kV Bays -As per scope | Set | 1 | 1
| 26 | LT Switchgear
| 26.1 | 415V Main switchboard | Set | 1 | 1
| 26.2 | 415V ACDB | Set | 1 | 1
| 26.3 | 415V MLDB | Set | 1 | 1
| 26.4 | 415V Emergency LDB | Set | 1 | 1
| 26.5 | 415V Airconditioning DB | Set | 1 | 1
| 26.6 | 220V DCDB | Set | 1 | 1
| 26.7 | 48V DCDB | Set | 1 | 1
| 27 | Batteries/Battery Charger
| 27.1 | Batteries (Sizing shall be as per requirementof Technical Specification)
| 27.1.a | 220V Battery&Battery Charger | Sets | 2 | 2
| 27.1.b | 48V Battery& Battery Charger | Sets | 2 | 2
| 27.2 | Battery Charger (Sizing shall be as per requirementof Technical Specification)
| 27.2.a | 220V | Sets | 2 | 2
| 27.2.b | 48V | Sets | 2 | 2
| 28 | 1500 kVA DG or above Set along with control panel | Set | 2 | 2
| 29 | AC & Ventillation system (High wall type split AC unit - as per technical specification) | LOT | LOT | LOT
| 30. | Fire Protection System
| 30.1 | Pumping arrangement for hydrant system, complete with all piping, valves, fittings,etc. inside pump house | Set | 1 | 1
| 30.2 | Hydrant system, complete U/G piping and accessories etc. outside the Pump House. | Set | 1 | 1
| 30.3 | Portable extinguishers | Set | 1 | 1
| 30.4 | Smoke detection system | Set | 1 | 1
| 30.5 | Hydrant system and complete O/G & U/G piping and accessories etc. out side the pump house for: |  | - | -
| 30.5.1 | AC & DC Switchyard | Set | 1 | 1
| 30.6 | Nitrogen injection system with all piping arrangement for complete fire fighting for converter transformers, ICT and Shunt Reactors ( As applicable) | Sets | 1 | 1
| 31 | Illumination System
| 31.1 | Control Room Building Illumination | LOT | LOT | LOT
| 31.2 | DG set & fire fighting pumphouse building Illumination | LOT | LOT | LOT
| 31.3 | Switchyard Lighting | LOT | LS | LS
| 31.4 | Street Lighting | LOT | LS | LS
| 32 | Cables along with associated like clamps, glands, lugs and straight joints etc.
| 32.1 | HT Cable | LOT | LOT | LOT
| 32.1.1 | 33kV | LOT | NA | LOT
| 32.1.2 | 20kV | LOT | LOT | NA
| 32.2 | Power Cables & Control Cable | LOT | LOT | LOT
| 32.2.1 | Power Cable(PVC) for 500kV S/S | LOT | LOT | LOT
| 32.2.2 | Control Cable (PVC) for 500kV S/S | LOT | LOT | LOT
| 32.2.3 | Power Cable(PVC) for 220 kV S/S | LOT | LOT | LOT
| 32.2.4 | Control Cable (PVC) for 220 kV S/S | LOT | LOT | LOT
| 33 | 40 mm MS rod for Earthmat | LOT | LOT | LOT
| 34 | Steel Structures for 500 kV S/S
| 34.1 | Lattice Structure (excluding CB structure) | LOT | LOT | LOT
| 34.2 | Pipe structure | LOT | LOT | LOT
| 35 | Steel Structures for 220 kV S/S
| 35.1 | Lattice Structure (excluding CB structure) | LOT | LOT | LOT
| 35.2 | Pipe structure | LOT | LOT | LOT
| 36. | Civil Works including RCC foundation and buildings (As per scope of technical specification for all equipments and buildings) | LOT | LOT | LOT
| 37 | Cable Trench including all types of crossings | LOT | LOT | LOT
| 38 | Soil Investigation | LOT | LOT | LOT
| 39 | Site surfacing (gravelling) & Anti weed treatment | LOT | LOT | LOT
| 40 | Wide Roads (including all crossings) | LOT | LOT | LOT
| 41 | Storm water drainage including culverts | LOT | LOT | LOT
| 42 | Switchyard Fencing along with gates | LOT | LOT | LOT
| 43 | Public Address System | LOT | LOT | LOT
| 44 | Water Treatment Plant/Supply System | LOT | LOT | LOT
| 45 | Oil Handling System | LOT | LOT | LOT
| 46 | Transformer oil processing plant /drying air | LOT | LOT | LOT
| 47 | Valve Cooling System(Pole basis) | LOT | LOT | LOT
| 48 | Building Management System | LOT | LOT | LOT
| 49 | Tyre mounted Hydraulic operated telescopic crane | LOT | LOT | LOT
| 50 | O & M TOOLS AND Tackles | LOT | LOT | LOT
| 51 | Circuit Breaker SF6 gas filling and evacuation plant | LOT | LOT | LOT
| 52 | UPS System for Converter Station | LOT | LOT | LOT
| 53 | Mandatory Spares as per Chapter 1 of employers requirement part II | LOT | LOT | LOT
| 54 | Test Equipments as per Chapter 9 of employers requirement part II | LOT | LOT | LOT
| 55 | Any other item not covered above but required for satisfactory operation of HVDC System shall be supplied by the contractor and will be included in BOQ by the bidder
The current rating/size/type may change as per studies during detailed engineering
| Note 1 | The bill of quantiy stipulated above is indicative - The bidder shall work out the bill of quantity in detail as per the specification and indicate in their first stage Bid.
| Note 2 | The bidder shall clearly understand that any additional equipment / material required for successful operaiton of the HVDC system shall be provided by the bidder without any additional cost to the employer
| Note 3 | The Bidder shall provide PLCC repeater stations as required along with all equipment & material and shall enclose the detail BOQ in Stage One bid